## Building
Zone Summary
	Area [m2]	Part of Total Floor Area (Y/N)	Volume [m3]	Window Glass Area [m2]	Opening Area [m2]	Lighting [W/m2]	People [m2 per person]	Plug and Process [W/m2]
CORE_BOTTOM	983.54	Yes	2698.04	0	0	10.76	18.58	43.4074
CORE_MID	983.54	Yes	2698.04	0	0	10.76	18.58	10.76
CORE_TOP	983.54	Yes	2698.04	0	0	10.76	18.58	10.76
FIRSTFLOOR_PLENUM	1660.73	No	2024.76	0	0	0		0
MIDFLOOR_PLENUM	1660.73	No	2024.76	0	0	0		0
PERIMETER_BOT_ZN_1	207.34	Yes	568.77	65.28	65.28	10.76	18.58	10.76
PERIMETER_BOT_ZN_2	131.26	Yes	360.08	43.52	43.52	10.76	18.58	10.76
PERIMETER_BOT_ZN_3	207.34	Yes	568.77	65.28	65.28	10.76	18.58	10.76
PERIMETER_BOT_ZN_4	131.25	Yes	360.05	43.52	43.52	10.76	18.58	10.76
PERIMETER_MID_ZN_1	207.34	Yes	568.77	65.28	65.28	10.76	18.58	10.76
PERIMETER_MID_ZN_2	131.26	Yes	360.08	43.52	43.52	10.76	18.58	10.76
PERIMETER_MID_ZN_3	207.34	Yes	568.77	65.28	65.28	10.76	18.58	10.76
PERIMETER_MID_ZN_4	131.25	Yes	360.05	43.52	43.52	10.76	18.58	10.76
PERIMETER_TOP_ZN_1	207.34	Yes	568.77	65.28	65.28	10.76	18.58	10.76
PERIMETER_TOP_ZN_2	131.26	Yes	360.08	43.52	43.52	10.76	18.58	10.76
PERIMETER_TOP_ZN_3	207.34	Yes	568.77	65.28	65.28	10.76	18.58	10.76
PERIMETER_TOP_ZN_4	131.25	Yes	360.05	43.52	43.52	10.76	18.58	10.76
TOPFLOOR_PLENUM	1660.73	No	2024.76	0	0	0		0
Total	4982.19		13667.13	652.83	652.83	10.76	18.58	17.2049
Conditioned Total	4982.19		13667.13	652.83	652.83	10.76	18.58	17.2049
Unconditioned Total	0		0	0	0
Not Part of Total	4982.19		6074.28	0	0	0		0

## VAV
AirTerminal:SingleDuct:VAV:Reheat					Cooling Coils
	Design Size Maximum Air Flow Rate [m3/s]	Design Size Constant Minimum Air Flow Fraction	User-Specified Constant Minimum Air Flow Fraction	Design Size Minimum Air Flow Rate [m3/s]	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	Design Size Maximum Flow Fraction during Reheat []
CORE_BOTTOM VAV BOX COMPONENT	3.58	0.209426	0.3	1.07	0.001092	0.3
CORE_MID VAV BOX COMPONENT	3.47	0.215985	0.3	1.04	0.001058	0.3			Type	Design Coil Load [W]	Nominal Total Capacity [W]	Nominal Sensible Capacity [W]	Nominal Latent Capacity [W]	Nominal Sensible Heat Ratio	Nominal Efficiency [W/W]	Nominal Coil UA Value [W/C]	Nominal Coil Surface Area [m2]
CORE_TOP VAV BOX COMPONENT	3.29	0.227769	0.3	0.987124	0.001004	0.3		VAV_1_COOLC DXCOIL	Coil:Cooling:DX:TwoSpeed		118981.01	95262.77	23718.24	0.8	3.23
PERIMETER_BOT_ZN_1 VAV BOX COMPONENT	0.940984	0.2	0.3	0.282295	0.001362	0.3		VAV_2_COOLC DXCOIL	Coil:Cooling:DX:TwoSpeed		130564.76	104537.36	26027.4	0.8	3.23
PERIMETER_BOT_ZN_2 VAV BOX COMPONENT	0.958392	0.2	0.3	0.287517	0.00219	0.3		VAV_3_COOLC DXCOIL	Coil:Cooling:DX:TwoSpeed		129320.99	103571.55	25749.44	0.8	3.23
PERIMETER_BOT_ZN_3 VAV BOX COMPONENT	0.594831	0.265608	0.3	0.178449	0.000861	0.3		Nominal values are gross at rated conditions, i.e., the supply air fan heat and electric power NOT accounted for.
PERIMETER_BOT_ZN_4 VAV BOX COMPONENT	1.11	0.2	0.3	0.334447	0.002548	0.3
PERIMETER_MID_ZN_1 VAV BOX COMPONENT	1.18	0.2	0.3	0.35536	0.001714	0.3		DX Cooling Coils
PERIMETER_MID_ZN_2 VAV BOX COMPONENT	1.14	0.2	0.3	0.341524	0.002602	0.3
PERIMETER_MID_ZN_3 VAV BOX COMPONENT	0.81856	0.2	0.3	0.245568	0.001184	0.3
PERIMETER_MID_ZN_4 VAV BOX COMPONENT	1.28	0.2	0.3	0.382789	0.002916	0.3					DX Cooling Coil Type	Standard Rated Net Cooling Capacity [W]	Standard Rated Net COP [W/W]	EER [Btu/W-h]	SEER User [Btu/W-h]	SEER Standard [Btu/W-h]	IEER [Btu/W-h]
PERIMETER_TOP_ZN_1 VAV BOX COMPONENT	1.18	0.2	0.3	0.352642	0.001701	0.3		VAV_1_COOLC DXCOIL					113245.7	2.67	9.12	N/A	N/A	11.19
PERIMETER_TOP_ZN_2 VAV BOX COMPONENT	1.07	0.2	0.3	0.321816	0.002452	0.3		VAV_2_COOLC DXCOIL					124271.1	2.67	9.12	N/A	N/A	11.19
PERIMETER_TOP_ZN_3 VAV BOX COMPONENT	0.910809	0.2	0.3	0.273243	0.001318	0.3		VAV_3_COOLC DXCOIL					123116.3	2.68	9.13	N/A	N/A	11.2
PERIMETER_TOP_ZN_4 VAV BOX COMPONENT	1.33	0.2	0.3	0.39759	0.003029	0.3

Coil:Heating:Electric

	Design Size Nominal Capacity [W]
CORE_BOTTOM VAV BOX REHEAT COIL	36038.79
CORE_MID VAV BOX REHEAT COIL	34944.45
CORE_TOP VAV BOX REHEAT COIL	38173.08
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL	13485.04
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL	9651.58
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL	13352.1
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL	11226.96
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL	14311.97
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL	11464.52
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL	14173.32
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL	12849.71
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL	20278.29
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL	13258.82
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL	20162.57
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL	13346.57

AirLoopHVAC

	Sum of Air Terminal Maximum Heating Flow Rates [m3/s]	Sum of Air Terminal Minimum Heating Flow Rates [m3/s]	Sum of Air Terminal Maximum Flow Rates [m3/s]	Adjusted Heating Design Air Flow Rate [m3/s]	Adjusted Cooling Design Air Flow Rate [m3/s]	Adjusted Main Design Air Flow Rate [m3/s]	User Heating Air Flow Ratio []	Calculated Heating Air Flow Ratio []	Design Supply Air Flow Rate [m3/s]
VAV_1	2.16	2.16	7.19	2.16	7.19	7.19	0.3	0.3	7.19
VAV_2	2.37	2.37	7.89	2.37	7.89	7.89	0.3	0.3	7.89
VAV_3	2.33	2.33	7.77	3.13	7.77	7.77	0.3	0.402854	7.77

Controller:OutdoorAir

	Maximum Outdoor Air Flow Rate [m3/s]	Minimum Outdoor Air Flow Rate [m3/s]
VAV_1_OA_CONTROLLER	7.19	1.12
VAV_2_OA_CONTROLLER	7.89	1.12
VAV_3_OA_CONTROLLER	7.77	1.12

Coil:Cooling:DX:TwoSpeed

	Design Size High Speed Rated Air Flow Rate [m3/s]	Design Size High Speed Gross Rated Total Cooling Capacity [W]	Design Size High Speed Rated Sensible Heat Ratio	Design Size Low Speed Rated Air Flow Rate [m3/s]	Design Size Low Speed Gross Rated Total Cooling Capacity [W]	Design Size Low Speed Gross Rated Sensible Heat Ratio
VAV_1_COOLC DXCOIL	7.19	118981.01	0.800655	2.4	39656.37	0.800655
VAV_2_COOLC DXCOIL	7.89	130564.76	0.800655	2.63	43517.23	0.800655
VAV_3_COOLC DXCOIL	7.77	129320.99	0.800887	2.59	43102.69	0.800887

Coil:Heating:Fuel

	Design Size Nominal Capacity [W]
VAV_1_HEATC	34745.85
VAV_2_HEATC	33850.15
VAV_3_HEATC	33993.76

Fan:VariableVolume

	Design Size Maximum Flow Rate [m3/s]
VAV_1_FAN	7.19
VAV_2_FAN	7.89
VAV_3_FAN	7.77

Zone Sizing Information

	Zone Name	Load Type	Calc Des Load {W}	User Des Load {W}	Calc Des Air Flow Rate {m3/s}	User Des Air Flow Rate {m3/s}	Design Day Name	Date/Time of Peak	Temperature at Peak {C}	Humidity Ratio at Peak {kgWater/kgDryAir}	Floor Area {m2}	# Occupants	Calc Outdoor Air Flow Rate {m3/s}	Calc DOAS Heat Addition Rate {W}
1	CORE_BOTTOM	Cooling	30398.43824	40429.92286	2.69069	3.57861	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 09:00:00	19.04	0.0127959	983.53657	52.93523	0.66169	0
2	CORE_BOTTOM	Heating	6386.99965	8494.70953	0.21848	0.66169	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:10:00	-18.6	0.000883816	983.53657	52.93523	0.66169	0
3	CORE_MID	Cooling	30010.70187	39914.23349	2.60898	3.46995	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 07:00:00	13.568	0.011845	983.53657	52.93523	0.66169	0
4	CORE_MID	Heating	7760.67606	10321.69915	0.26547	0.66169	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:10:00	-18.6	0.000883816	983.53657	52.93523	0.66169	0
5	CORE_TOP	Cooling	27951.72138	37175.78943	2.474	3.29041	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 18:40:00	22.232	0.0128015	983.53657	52.93523	0.66169	0
6	CORE_TOP	Heating	24995.35307	33243.81958	0.85501	1.13716	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:10:00	-18.6	0.000883816	983.53657	52.93523	0.66169	0
7	PERIMETER_BOT_ZN_1	Cooling	7993.55297	10631.42546	0.70751	0.94098	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 13:30:00	27.02	0.01281	207.33814	11.15921	0.13949	0
8	PERIMETER_BOT_ZN_1	Heating	8831.98784	11746.54383	0.30204	0.40171	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	207.33814	11.15921	0.13949	0
9	PERIMETER_BOT_ZN_2	Cooling	8141.60634	10828.33644	0.7206	0.95839	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 09:00:00	19.04	0.0127959	131.26219	7.0647	0.0883088	0
10	PERIMETER_BOT_ZN_2	Heating	5850.24241	7780.8224	0.20007	0.26609	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	131.26219	7.0647	0.0883088	0
11	PERIMETER_BOT_ZN_3	Cooling	5052.89617	6720.3519	0.44724	0.59483	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 18:20:00	22.992	0.0128029	207.33814	11.15921	0.13949	0
12	PERIMETER_BOT_ZN_3	Heating	8744.92219	11630.74652	0.29906	0.39775	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	207.33814	11.15921	0.13949	0
13	PERIMETER_BOT_ZN_4	Cooling	9470.57111	12595.85957	0.83821	1.11482	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 17:10:00	25.01867	0.0128065	131.25358	7.06424	0.088303	0
14	PERIMETER_BOT_ZN_4	Heating	5884.07724	7825.82273	0.20123	0.26763	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	131.25358	7.06424	0.088303	0
15	PERIMETER_MID_ZN_1	Cooling	10062.61513	13383.27812	0.89063	1.18453	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 13:20:00	26.89333	0.0128098	207.33814	11.15921	0.13949	0
16	PERIMETER_MID_ZN_1	Heating	9373.56409	12466.84025	0.32056	0.42635	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	207.33814	11.15921	0.13949	0
17	PERIMETER_MID_ZN_2	Cooling	9670.99625	12862.42502	0.85595	1.13841	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 09:00:00	19.04	0.0127959	131.26219	7.0647	0.0883088	0
18	PERIMETER_MID_ZN_2	Heating	6206.78228	8255.02043	0.21226	0.28231	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	131.26219	7.0647	0.0883088	0
19	PERIMETER_MID_ZN_3	Cooling	6953.56636	9248.24326	0.61546	0.81856	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 15:00:00	27.4	0.0128107	207.33814	11.15921	0.13949	0
20	PERIMETER_MID_ZN_3	Heating	9282.76015	12346.07101	0.31746	0.42222	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	207.33814	11.15921	0.13949	0
21	PERIMETER_MID_ZN_4	Cooling	10839.52116	14416.56314	0.95937	1.27596	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 17:10:00	25.01867	0.0128065	131.25358	7.06424	0.088303	0
22	PERIMETER_MID_ZN_4	Heating	6225.14759	8279.4463	0.21289	0.28314	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	131.25358	7.06424	0.088303	0
23	PERIMETER_TOP_ZN_1	Cooling	9985.62778	13280.88495	0.88381	1.17547	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 13:50:00	27.27333	0.0128105	207.33814	11.15921	0.13949	0
24	PERIMETER_TOP_ZN_1	Heating	13281.01096	17663.74458	0.4542	0.60408	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	207.33814	11.15921	0.13949	0
25	PERIMETER_TOP_ZN_2	Cooling	9112.88931	12120.14278	0.80656	1.07272	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 09:00:00	19.04	0.0127959	131.26219	7.0647	0.0883088	0
26	PERIMETER_TOP_ZN_2	Heating	8683.76364	11549.40565	0.29697	0.39498	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	131.26219	7.0647	0.0883088	0
27	PERIMETER_TOP_ZN_3	Cooling	7737.22833	10290.51368	0.68482	0.91081	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 18:20:00	22.992	0.0128029	207.33814	11.15921	0.13949	0
28	PERIMETER_TOP_ZN_3	Heating	13205.22546	17562.94987	0.45161	0.60064	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	207.33814	11.15921	0.13949	0
29	PERIMETER_TOP_ZN_4	Cooling	11258.67032	14974.03153	0.99647	1.3253	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 17:10:00	25.01867	0.0128065	131.25358	7.06424	0.088303	0
30	PERIMETER_TOP_ZN_4	Heating	8689.05589	11556.44433	0.29716	0.39522	BOULDER ANN HTG 99.6% CONDNS DB	12/21 06:00:00	-18.6	0.000883816	131.25358	7.06424	0.088303	0

System Sizing Information

	System Name	Load Type	Peak Load Kind	User Design Capacity	Calc Des Air Flow Rate [m3/s]	User Des Air Flow Rate [m3/s]	Design Day Name	Date/Time of Peak
1	VAV_1	Cooling	Sensible	84899.15	7.18764	7.18764	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 05:00:00
2	VAV_1	Heating	Sensible	35434.58	1.99488	1.99488	BOULDER ANN HTG 99.6% CONDNS DB	12/21 13:10:00
3	VAV_2	Cooling	Sensible	91357.99	7.88742	7.88742	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 05:00:00
4	VAV_2	Heating	Sensible	35089.74	2.07571	2.07571	BOULDER ANN HTG 99.6% CONDNS DB	12/21 18:00:00
5	VAV_3	Cooling	Sensible	93515.71	7.77472	7.77472	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 05:00:00
6	VAV_3	Heating	Sensible	30581.31	3.13208	3.13208	BOULDER ANN HTG 99.6% CONDNS DB	12/21 18:00:00

Component Sizing Information

	Component Type	Component Name	Input Field Description	Value
1	AirTerminal:SingleDuct:VAV:Reheat	CORE_BOTTOM VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	3.57861
2	AirTerminal:SingleDuct:VAV:Reheat	CORE_BOTTOM VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.20943
3	AirTerminal:SingleDuct:VAV:Reheat	CORE_BOTTOM VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
4	AirTerminal:SingleDuct:VAV:Reheat	CORE_BOTTOM VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	1.07358
5	AirTerminal:SingleDuct:VAV:Reheat	CORE_BOTTOM VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00109155
6	AirTerminal:SingleDuct:VAV:Reheat	CORE_BOTTOM VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
7	Coil:Heating:Electric	CORE_BOTTOM VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	36038.78599
8	AirTerminal:SingleDuct:VAV:Reheat	CORE_MID VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	3.46995
9	AirTerminal:SingleDuct:VAV:Reheat	CORE_MID VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.21598
10	AirTerminal:SingleDuct:VAV:Reheat	CORE_MID VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
11	AirTerminal:SingleDuct:VAV:Reheat	CORE_MID VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	1.04098
12	AirTerminal:SingleDuct:VAV:Reheat	CORE_MID VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00105841
13	AirTerminal:SingleDuct:VAV:Reheat	CORE_MID VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
14	Coil:Heating:Electric	CORE_MID VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	34944.45166
15	AirTerminal:SingleDuct:VAV:Reheat	CORE_TOP VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	3.29041
16	AirTerminal:SingleDuct:VAV:Reheat	CORE_TOP VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.22777
17	AirTerminal:SingleDuct:VAV:Reheat	CORE_TOP VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
18	AirTerminal:SingleDuct:VAV:Reheat	CORE_TOP VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.98712
19	AirTerminal:SingleDuct:VAV:Reheat	CORE_TOP VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00100365
20	AirTerminal:SingleDuct:VAV:Reheat	CORE_TOP VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
21	Coil:Heating:Electric	CORE_TOP VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	38173.07559
22	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_1 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	0.94098
23	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_1 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.2
24	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_1 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
25	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_1 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.2823
26	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_1 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00136152
27	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_1 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
28	Coil:Heating:Electric	PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	13485.0432
29	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_2 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	0.95839
30	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_2 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.2
31	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_2 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
32	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_2 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.28752
33	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_2 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00219041
34	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_2 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
35	Coil:Heating:Electric	PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	9651.58483
36	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_3 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	0.59483
37	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_3 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.26561
38	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_3 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
39	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_3 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.17845
40	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_3 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.000860668
41	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_3 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
42	Coil:Heating:Electric	PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	13352.10129
43	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_4 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	1.11482
44	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_4 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.2
45	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_4 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
46	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_4 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.33445
47	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_4 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.0025481
48	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_BOT_ZN_4 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
49	Coil:Heating:Electric	PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	11226.95969
50	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_1 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	1.18453
51	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_1 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.2
52	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_1 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
53	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_1 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.35536
54	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_1 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00171392
55	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_1 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
56	Coil:Heating:Electric	PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	14311.97342
57	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_2 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	1.13841
58	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_2 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.2
59	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_2 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
60	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_2 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.34152
61	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_2 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00260185
62	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_2 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
63	Coil:Heating:Electric	PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	11464.52482
64	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_3 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	0.81856
65	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_3 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.2
66	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_3 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
67	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_3 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.24557
68	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_3 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00118438
69	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_3 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
70	Coil:Heating:Electric	PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	14173.32354
71	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_4 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	1.27596
72	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_4 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.2
73	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_4 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
74	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_4 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.38279
75	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_4 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00291641
76	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_MID_ZN_4 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
77	Coil:Heating:Electric	PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	12849.71091
78	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_1 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	1.17547
79	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_1 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.2
80	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_1 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
81	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_1 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.35264
82	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_1 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.0017008
83	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_1 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
84	Coil:Heating:Electric	PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	20278.29341
85	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_2 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	1.07272
86	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_2 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.2
87	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_2 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
88	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_2 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.32182
89	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_2 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.0024517
90	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_2 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
91	Coil:Heating:Electric	PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	13258.8208
92	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_3 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	0.91081
93	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_3 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.2
94	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_3 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
95	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_3 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.27324
96	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_3 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00131786
97	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_3 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
98	Coil:Heating:Electric	PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	20162.56905
99	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_4 VAV BOX COMPONENT	Design Size Maximum Air Flow Rate [m3/s]	1.3253
100	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_4 VAV BOX COMPONENT	Design Size Constant Minimum Air Flow Fraction	0.2
101	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_4 VAV BOX COMPONENT	User-Specified Constant Minimum Air Flow Fraction	0.3
102	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_4 VAV BOX COMPONENT	Design Size Minimum Air Flow Rate [m3/s]	0.39759
103	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_4 VAV BOX COMPONENT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00302917
104	AirTerminal:SingleDuct:VAV:Reheat	PERIMETER_TOP_ZN_4 VAV BOX COMPONENT	Design Size Maximum Flow Fraction during Reheat []	0.3
105	Coil:Heating:Electric	PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL	Design Size Nominal Capacity [W]	13346.57362
106	AirLoopHVAC	VAV_1	Sum of Air Terminal Maximum Heating Flow Rates [m3/s]	2.15629
107	AirLoopHVAC	VAV_1	Sum of Air Terminal Minimum Heating Flow Rates [m3/s]	2.15629
108	AirLoopHVAC	VAV_1	Sum of Air Terminal Maximum Flow Rates [m3/s]	7.18764
109	AirLoopHVAC	VAV_1	Adjusted Heating Design Air Flow Rate [m3/s]	2.15629
110	AirLoopHVAC	VAV_1	Adjusted Cooling Design Air Flow Rate [m3/s]	7.18764
111	AirLoopHVAC	VAV_1	Adjusted Main Design Air Flow Rate [m3/s]	7.18764
112	AirLoopHVAC	VAV_1	User Heating Air Flow Ratio []	0.3
113	AirLoopHVAC	VAV_1	Calculated Heating Air Flow Ratio []	0.3
114	AirLoopHVAC	VAV_2	Sum of Air Terminal Maximum Heating Flow Rates [m3/s]	2.36623
115	AirLoopHVAC	VAV_2	Sum of Air Terminal Minimum Heating Flow Rates [m3/s]	2.36623
116	AirLoopHVAC	VAV_2	Sum of Air Terminal Maximum Flow Rates [m3/s]	7.88742
117	AirLoopHVAC	VAV_2	Adjusted Heating Design Air Flow Rate [m3/s]	2.36623
118	AirLoopHVAC	VAV_2	Adjusted Cooling Design Air Flow Rate [m3/s]	7.88742
119	AirLoopHVAC	VAV_2	Adjusted Main Design Air Flow Rate [m3/s]	7.88742
120	AirLoopHVAC	VAV_2	User Heating Air Flow Ratio []	0.3
121	AirLoopHVAC	VAV_2	Calculated Heating Air Flow Ratio []	0.3
122	AirLoopHVAC	VAV_3	Sum of Air Terminal Maximum Heating Flow Rates [m3/s]	2.33241
123	AirLoopHVAC	VAV_3	Sum of Air Terminal Minimum Heating Flow Rates [m3/s]	2.33241
124	AirLoopHVAC	VAV_3	Sum of Air Terminal Maximum Flow Rates [m3/s]	7.77472
125	AirLoopHVAC	VAV_3	Adjusted Heating Design Air Flow Rate [m3/s]	3.13208
126	AirLoopHVAC	VAV_3	Adjusted Cooling Design Air Flow Rate [m3/s]	7.77472
127	AirLoopHVAC	VAV_3	Adjusted Main Design Air Flow Rate [m3/s]	7.77472
128	AirLoopHVAC	VAV_3	User Heating Air Flow Ratio []	0.3
129	AirLoopHVAC	VAV_3	Calculated Heating Air Flow Ratio []	0.40285
130	AirLoopHVAC	VAV_1	Design Supply Air Flow Rate [m3/s]	7.18764
131	AirLoopHVAC	VAV_2	Design Supply Air Flow Rate [m3/s]	7.88742
132	AirLoopHVAC	VAV_3	Design Supply Air Flow Rate [m3/s]	7.77472
133	Controller:OutdoorAir	VAV_1_OA_CONTROLLER	Maximum Outdoor Air Flow Rate [m3/s]	7.18764
134	Controller:OutdoorAir	VAV_1_OA_CONTROLLER	Minimum Outdoor Air Flow Rate [m3/s]	1.11728
135	Coil:Cooling:DX:TwoSpeed	VAV_1_COOLC DXCOIL	Design Size High Speed Rated Air Flow Rate [m3/s]	7.18764
136	Coil:Cooling:DX:TwoSpeed	VAV_1_COOLC DXCOIL	Design Size High Speed Gross Rated Total Cooling Capacity [W]	118981.00762
137	Coil:Cooling:DX:TwoSpeed	VAV_1_COOLC DXCOIL	Design Size High Speed Rated Sensible Heat Ratio	0.80066
138	Coil:Cooling:DX:TwoSpeed	VAV_1_COOLC DXCOIL	Design Size Low Speed Rated Air Flow Rate [m3/s]	2.39564
139	Coil:Cooling:DX:TwoSpeed	VAV_1_COOLC DXCOIL	Design Size Low Speed Gross Rated Total Cooling Capacity [W]	39656.36984
140	Coil:Cooling:DX:TwoSpeed	VAV_1_COOLC DXCOIL	Design Size Low Speed Gross Rated Sensible Heat Ratio	0.80066
141	Coil:Heating:Fuel	VAV_1_HEATC	Design Size Nominal Capacity [W]	34745.84982
142	Fan:VariableVolume	VAV_1_FAN	Design Size Maximum Flow Rate [m3/s]	7.18764
143	Controller:OutdoorAir	VAV_2_OA_CONTROLLER	Maximum Outdoor Air Flow Rate [m3/s]	7.88742
144	Controller:OutdoorAir	VAV_2_OA_CONTROLLER	Minimum Outdoor Air Flow Rate [m3/s]	1.11728
145	Coil:Cooling:DX:TwoSpeed	VAV_2_COOLC DXCOIL	Design Size High Speed Rated Air Flow Rate [m3/s]	7.88742
146	Coil:Cooling:DX:TwoSpeed	VAV_2_COOLC DXCOIL	Design Size High Speed Gross Rated Total Cooling Capacity [W]	130564.75998
147	Coil:Cooling:DX:TwoSpeed	VAV_2_COOLC DXCOIL	Design Size High Speed Rated Sensible Heat Ratio	0.80066
148	Coil:Cooling:DX:TwoSpeed	VAV_2_COOLC DXCOIL	Design Size Low Speed Rated Air Flow Rate [m3/s]	2.62888
149	Coil:Cooling:DX:TwoSpeed	VAV_2_COOLC DXCOIL	Design Size Low Speed Gross Rated Total Cooling Capacity [W]	43517.2345
150	Coil:Cooling:DX:TwoSpeed	VAV_2_COOLC DXCOIL	Design Size Low Speed Gross Rated Sensible Heat Ratio	0.80066
151	Coil:Heating:Fuel	VAV_2_HEATC	Design Size Nominal Capacity [W]	33850.15495
152	Fan:VariableVolume	VAV_2_FAN	Design Size Maximum Flow Rate [m3/s]	7.88742
153	Controller:OutdoorAir	VAV_3_OA_CONTROLLER	Maximum Outdoor Air Flow Rate [m3/s]	7.77472
154	Controller:OutdoorAir	VAV_3_OA_CONTROLLER	Minimum Outdoor Air Flow Rate [m3/s]	1.11728
155	Coil:Cooling:DX:TwoSpeed	VAV_3_COOLC DXCOIL	Design Size High Speed Rated Air Flow Rate [m3/s]	7.77472
156	Coil:Cooling:DX:TwoSpeed	VAV_3_COOLC DXCOIL	Design Size High Speed Gross Rated Total Cooling Capacity [W]	129320.98797
157	Coil:Cooling:DX:TwoSpeed	VAV_3_COOLC DXCOIL	Design Size High Speed Rated Sensible Heat Ratio	0.80089
158	Coil:Cooling:DX:TwoSpeed	VAV_3_COOLC DXCOIL	Design Size Low Speed Rated Air Flow Rate [m3/s]	2.59131
159	Coil:Cooling:DX:TwoSpeed	VAV_3_COOLC DXCOIL	Design Size Low Speed Gross Rated Total Cooling Capacity [W]	43102.68529
160	Coil:Cooling:DX:TwoSpeed	VAV_3_COOLC DXCOIL	Design Size Low Speed Gross Rated Sensible Heat Ratio	0.80089
161	Coil:Heating:Fuel	VAV_3_HEATC	Design Size Nominal Capacity [W]	33993.76243
162	Fan:VariableVolume	VAV_3_FAN	Design Size Maximum Flow Rate [m3/s]	7.77472
163	PlantLoop	SWHSYS1	Maximum Loop Flow Rate [m3/s]	3.12E-05
164	PlantLoop	SWHSYS1	Plant Loop Volume [m3]	0.003744
165	Pump:ConstantSpeed	SWHSYS1 PUMP	Design Flow Rate [m3/s]	3.12E-05
166	Pump:ConstantSpeed	SWHSYS1 PUMP	Design Power Consumption [W]	8.44009
167	WaterHeater:Mixed	SWHSYS1 WATER HEATER	Use Side Design Flow Rate [m3/s]	3.12E-05

VAV DX Cooling Coil Standard Rating Information

	DX Coil Type	DX Coil Name	Fan Type	Fan Name	Standard Net Cooling Capacity {W}	Standard Net Cooling Capacity {Btu/h}	IEER {Btu/W-h}	COP 100% Capacity {W/W}	COP 75% Capacity {W/W}	COP 50% Capacity {W/W}	COP 25% Capacity {W/W}	EER 100% Capacity {Btu/W-h}	EER 75% Capacity {Btu/W-h}	EER 50% Capacity {Btu/W-h}	EER 25% Capacity {Btu/W-h}	Supply Air Flow 100% {kg/s}	Supply Air Flow 75% {kg/s}	Supply Air Flow 50% {kg/s}	Supply Air Flow 25% {kg/s}
1	Coil:Cooling:DX:TwoSpeed	VAV_1_COOLC DXCOIL	N/A	N/A	113245.7	386410.37	11.19	2.67	3.13	3.52	3.65	9.12	10.67	12.03	12.47	6.825	5.4524	3.6293	1.5317
2	Coil:Cooling:DX:TwoSpeed	VAV_2_COOLC DXCOIL	N/A	N/A	124271.07	424030.51	11.19	2.67	3.13	3.52	3.65	9.12	10.67	12.03	12.47	7.4894	5.9832	3.9826	1.6808
3	Coil:Cooling:DX:TwoSpeed	VAV_3_COOLC DXCOIL	N/A	N/A	123116.31	420090.28	11.2	2.68	3.13	3.53	3.66	9.13	10.68	12.04	12.48	7.3824	5.899	3.9273	1.655

Heating Coils

	Type	Design Coil Load [W]	Nominal Total Capacity [W]	Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL	Coil:Heating:Electric		36038.79	1
CORE_MID VAV BOX REHEAT COIL	Coil:Heating:Electric		34944.45	1
CORE_TOP VAV BOX REHEAT COIL	Coil:Heating:Electric		38173.08	1
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL	Coil:Heating:Electric		13485.04	1
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL	Coil:Heating:Electric		9651.58	1
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL	Coil:Heating:Electric		13352.1	1
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL	Coil:Heating:Electric		11226.96	1
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL	Coil:Heating:Electric		14311.97	1
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL	Coil:Heating:Electric		11464.52	1
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL	Coil:Heating:Electric		14173.32	1
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL	Coil:Heating:Electric		12849.71	1
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL	Coil:Heating:Electric		20278.29	1
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL	Coil:Heating:Electric		13258.82	1
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL	Coil:Heating:Electric		20162.57	1
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL	Coil:Heating:Electric		13346.57	1
VAV_1_HEATC	Coil:Heating:Fuel		34745.85	0.8
VAV_2_HEATC	Coil:Heating:Fuel		33850.15	0.8
VAV_3_HEATC	Coil:Heating:Fuel		33993.76	0.8

Fans

				Type	Total Efficiency [W/W]	Delta Pressure [pa]	Max Air Flow Rate [m3/s]	Rated Electricity Rate [W]	Rated Power Per Max Air Flow Rate [W-s/m3]	Motor Heat In Air Fraction	Fan Energy Index	End Use Subcategory	Design Day Name for Fan Sizing Peak	Date/Time for Fan Sizing Peak
VAV_1_FAN					Fan:VariableVolume	0.59	1109.65	7.19	13483.94	1875.99	1	1.12	Fan Energy	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 18:00:00
VAV_2_FAN					Fan:VariableVolume	0.59	1109.65	7.89	14796.71	1875.99	1	1.11	Fan Energy	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 15:40:00
VAV_3_FAN					Fan:VariableVolume	0.59	1109.65	7.77	14585.29	1875.99	1	1.11	Fan Energy	BOULDER ANN CLG .4% CONDNS WB=>MDB	7/21 17:10:00

VAV DX Cooling Standard Rating Details

	DX Cooling Coil Type	Assocated Fan	Net Cooling Capacity [W]	COP [W/W]	EER [Btu/W-h]	IEER [Btu/W-h]	Supply Air Flow 100% [kg/s]	COP 75% Capacity [W/W]	EER 75% Capacity [Btu/W-h]	Supply Air Flow 75% [kg/s]	COP 50% Capacity [W/W]	EER 50% Capacity [Btu/W-h]	Supply Air Flow 50% [kg/s]	COP 25% Capacity [W/W]	EER 25% Capacity [Btu/W-h]	Supply Air Flow 25% [kg/s]
VAV_1_COOLC DXCOIL	Coil:Cooling:DX:TwoSpeed	None	113245.7	2.67	9.12	11.19	6.825	3.13	10.67	5.4524	3.52	12.03	3.6293	3.65	12.47	1.5317
VAV_2_COOLC DXCOIL	Coil:Cooling:DX:TwoSpeed	None	124271.07	2.67	9.12	11.19	7.4894	3.13	10.67	5.9832	3.52	12.03	3.9826	3.65	12.47	1.6808
VAV_3_COOLC DXCOIL	Coil:Cooling:DX:TwoSpeed	None	123116.31	2.68	9.13	11.2	7.3824	3.13	10.68	5.899	3.53	12.04	3.9273	3.66	12.48	1.655

## Zones
Zone Internal Gains Nominal

	Zone Name	Floor Area {m2}	# Occupants	Area per Occupant {m2/person}	Occupant per Area {person/m2}	Interior Lighting {W/m2}	Electric Load {W/m2}	Gas Load {W/m2}	Other Load {W/m2}	Hot Water Eq {W/m2}	Steam Equipment {W/m2}	Sum Loads per Area {W/m2}	Outdoor Controlled Baseboard Heat
1	CORE_BOTTOM	983.54	52.9	18.58	0.05382	10.76	43.407	0	0	0	0	54.167	No
2	CORE_MID	983.54	52.9	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
3	CORE_TOP	983.54	52.9	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
4	FIRSTFLOOR_PLENUM	1660.73	0	N/A	0	0	0	0	0	0	0	0	No
5	MIDFLOOR_PLENUM	1660.73	0	N/A	0	0	0	0	0	0	0	0	No
6	PERIMETER_BOT_ZN_1	207.34	11.2	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
7	PERIMETER_BOT_ZN_2	131.26	7.1	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
8	PERIMETER_BOT_ZN_3	207.34	11.2	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
9	PERIMETER_BOT_ZN_4	131.25	7.1	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
10	PERIMETER_MID_ZN_1	207.34	11.2	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
11	PERIMETER_MID_ZN_2	131.26	7.1	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
12	PERIMETER_MID_ZN_3	207.34	11.2	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
13	PERIMETER_MID_ZN_4	131.25	7.1	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
14	PERIMETER_TOP_ZN_1	207.34	11.2	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
15	PERIMETER_TOP_ZN_2	131.26	7.1	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
16	PERIMETER_TOP_ZN_3	207.34	11.2	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
17	PERIMETER_TOP_ZN_4	131.25	7.1	18.58	0.05382	10.76	10.76	0	0	0	0	21.52	No
18	TOPFLOOR_PLENUM	1660.73	0	N/A	0	0	0	0	0	0	0	0	No

People Internal Gains Nominal

	Name	Schedule Name	Zone Name	Zone Floor Area {m2}	# Zone Occupants	Number of People {}	People/Floor Area {person/m2}	Floor Area per person {m2/person}	Fraction Radiant	Fraction Convected	Sensible Fraction Calculation	Activity level	ASHRAE 55 Warnings	Carbon Dioxide Generation Rate	Nominal Minimum Number of People	Nominal Maximum Number of People	MRT Calculation Type	Work Efficiency	Clothing Insulation Calculation Method	Clothing Insulation Calculation Method Schedule	Clothing	Air Velocity	Fanger Calculation	Pierce Calculation	KSU Calculation
1	CORE_BOTTOM PEOPLE	BLDG_OCC_SCH	CORE_BOTTOM	983.54	52.9	52.9	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	53	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
2	CORE_MID PEOPLE	BLDG_OCC_SCH	CORE_MID	983.54	52.9	52.9	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	53	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
3	CORE_TOP PEOPLE	BLDG_OCC_SCH	CORE_TOP	983.54	52.9	52.9	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	53	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
4	PERIMETER_BOT_ZN_1 PEOPLE	BLDG_OCC_SCH	PERIMETER_BOT_ZN_1	207.34	11.2	11.2	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	11	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
5	PERIMETER_BOT_ZN_2 PEOPLE	BLDG_OCC_SCH	PERIMETER_BOT_ZN_2	131.26	7.1	7.1	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	7	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
6	PERIMETER_BOT_ZN_3 PEOPLE	BLDG_OCC_SCH	PERIMETER_BOT_ZN_3	207.34	11.2	11.2	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	11	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
7	PERIMETER_BOT_ZN_4 PEOPLE	BLDG_OCC_SCH	PERIMETER_BOT_ZN_4	131.25	7.1	7.1	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	7	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
8	PERIMETER_MID_ZN_1 PEOPLE	BLDG_OCC_SCH	PERIMETER_MID_ZN_1	207.34	11.2	11.2	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	11	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
9	PERIMETER_MID_ZN_2 PEOPLE	BLDG_OCC_SCH	PERIMETER_MID_ZN_2	131.26	7.1	7.1	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	7	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
10	PERIMETER_MID_ZN_3 PEOPLE	BLDG_OCC_SCH	PERIMETER_MID_ZN_3	207.34	11.2	11.2	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	11	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
11	PERIMETER_MID_ZN_4 PEOPLE	BLDG_OCC_SCH	PERIMETER_MID_ZN_4	131.25	7.1	7.1	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	7	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
12	PERIMETER_TOP_ZN_1 PEOPLE	BLDG_OCC_SCH	PERIMETER_TOP_ZN_1	207.34	11.2	11.2	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	11	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
13	PERIMETER_TOP_ZN_2 PEOPLE	BLDG_OCC_SCH	PERIMETER_TOP_ZN_2	131.26	7.1	7.1	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	7	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
14	PERIMETER_TOP_ZN_3 PEOPLE	BLDG_OCC_SCH	PERIMETER_TOP_ZN_3	207.34	11.2	11.2	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	11	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No
15	PERIMETER_TOP_ZN_4 PEOPLE	BLDG_OCC_SCH	PERIMETER_TOP_ZN_4	131.25	7.1	7.1	0.05382	18.58	0.3	0.7	AutoCalculate	ACTIVITY_SCH	No	3.82E-08	0	7	Zone Averaged	WORK_EFF_SCH	Clothing Insulation Schedule	N/A	CLOTHING_SCH	AIR_VELO_SCH	Yes	No	No

Lights Internal Gains Nominal

	Name	Schedule Name	Zone Name	Zone Floor Area {m2}	# Zone Occupants	Lighting Level {W}	Lights/Floor Area {W/m2}	Lights per person {W/person}	Fraction Return Air	Fraction Radiant	Fraction Short Wave	Fraction Convected	Fraction Replaceable	End-Use Category	Nominal Minimum Lighting Level {W}	Nominal Maximum Lighting Level {W}
1	CORE_BOTTOM_LIGHTS	BLDG_LIGHT_SCH	CORE_BOTTOM	983.54	52.9	10582.854	10.76	199.921	0.4	0.4	0.2	0	1	General	0	10582.854
2	CORE_MID_LIGHTS	BLDG_LIGHT_SCH	CORE_MID	983.54	52.9	10582.854	10.76	199.921	0.4	0.4	0.2	0	1	General	0	10582.854
3	CORE_TOP_LIGHTS	BLDG_LIGHT_SCH	CORE_TOP	983.54	52.9	10582.854	10.76	199.921	0.4	0.4	0.2	0	1	General	0	10582.854
4	PERIMETER_BOT_ZN_1_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_BOT_ZN_1	207.34	11.2	2230.958	10.76	199.921	0.4	0.4	0.2	0	1	General	0	2230.958
5	PERIMETER_BOT_ZN_2_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_BOT_ZN_2	131.26	7.1	1412.381	10.76	199.921	0.4	0.4	0.2	0	1	General	0	1412.381
6	PERIMETER_BOT_ZN_3_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_BOT_ZN_3	207.34	11.2	2230.958	10.76	199.921	0.4	0.4	0.2	0	1	General	0	2230.958
7	PERIMETER_BOT_ZN_4_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_BOT_ZN_4	131.25	7.1	1412.289	10.76	199.921	0.4	0.4	0.2	0	1	General	0	1412.289
8	PERIMETER_MID_ZN_1_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_MID_ZN_1	207.34	11.2	2230.958	10.76	199.921	0.4	0.4	0.2	0	1	General	0	2230.958
9	PERIMETER_MID_ZN_2_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_MID_ZN_2	131.26	7.1	1412.381	10.76	199.921	0.4	0.4	0.2	0	1	General	0	1412.381
10	PERIMETER_MID_ZN_3_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_MID_ZN_3	207.34	11.2	2230.958	10.76	199.921	0.4	0.4	0.2	0	1	General	0	2230.958
11	PERIMETER_MID_ZN_4_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_MID_ZN_4	131.25	7.1	1412.289	10.76	199.921	0.4	0.4	0.2	0	1	General	0	1412.289
12	PERIMETER_TOP_ZN_1_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_TOP_ZN_1	207.34	11.2	2230.958	10.76	199.921	0.4	0.4	0.2	0	1	General	0	2230.958
13	PERIMETER_TOP_ZN_2_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_TOP_ZN_2	131.26	7.1	1412.381	10.76	199.921	0.4	0.4	0.2	0	1	General	0	1412.381
14	PERIMETER_TOP_ZN_3_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_TOP_ZN_3	207.34	11.2	2230.958	10.76	199.921	0.4	0.4	0.2	0	1	General	0	2230.958
15	PERIMETER_TOP_ZN_4_LIGHTS	BLDG_LIGHT_SCH	PERIMETER_TOP_ZN_4	131.25	7.1	1412.289	10.76	199.921	0.4	0.4	0.2	0	1	General	0	1412.289

ElectricEquipment Internal Gains Nominal

	Name	Schedule Name	Zone Name	Zone Floor Area {m2}	# Zone Occupants	Equipment Level {W}	Equipment/Floor Area {W/m2}	Equipment per person {W/person}	Fraction Latent	Fraction Radiant	Fraction Lost	Fraction Convected	End-Use SubCategory	Nominal Minimum Equipment Level {W}	Nominal Maximum Equipment Level {W}
1	CORE_BOTTOM_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	CORE_BOTTOM	983.54	52.9	10582.854	10.76	199.921	0	0.5	0	0.5	General	0	10582.854
2	CORE_MID_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	CORE_MID	983.54	52.9	10582.854	10.76	199.921	0	0.5	0	0.5	General	0	10582.854
3	CORE_TOP_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	CORE_TOP	983.54	52.9	10582.854	10.76	199.921	0	0.5	0	0.5	General	0	10582.854
4	PERIMETER_BOT_ZN_1_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_BOT_ZN_1	207.34	11.2	2230.958	10.76	199.921	0	0.5	0	0.5	General	0	2230.958
5	PERIMETER_BOT_ZN_2_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_BOT_ZN_2	131.26	7.1	1412.381	10.76	199.921	0	0.5	0	0.5	General	0	1412.381
6	PERIMETER_BOT_ZN_3_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_BOT_ZN_3	207.34	11.2	2230.958	10.76	199.921	0	0.5	0	0.5	General	0	2230.958
7	PERIMETER_BOT_ZN_4_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_BOT_ZN_4	131.25	7.1	1412.289	10.76	199.921	0	0.5	0	0.5	General	0	1412.289
8	PERIMETER_MID_ZN_1_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_MID_ZN_1	207.34	11.2	2230.958	10.76	199.921	0	0.5	0	0.5	General	0	2230.958
9	PERIMETER_MID_ZN_2_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_MID_ZN_2	131.26	7.1	1412.381	10.76	199.921	0	0.5	0	0.5	General	0	1412.381
10	PERIMETER_MID_ZN_3_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_MID_ZN_3	207.34	11.2	2230.958	10.76	199.921	0	0.5	0	0.5	General	0	2230.958
11	PERIMETER_MID_ZN_4_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_MID_ZN_4	131.25	7.1	1412.289	10.76	199.921	0	0.5	0	0.5	General	0	1412.289
12	PERIMETER_TOP_ZN_1_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_TOP_ZN_1	207.34	11.2	2230.958	10.76	199.921	0	0.5	0	0.5	General	0	2230.958
13	PERIMETER_TOP_ZN_2_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_TOP_ZN_2	131.26	7.1	1412.381	10.76	199.921	0	0.5	0	0.5	General	0	1412.381
14	PERIMETER_TOP_ZN_3_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_TOP_ZN_3	207.34	11.2	2230.958	10.76	199.921	0	0.5	0	0.5	General	0	2230.958
15	PERIMETER_TOP_ZN_4_PLUGMISC_EQUIP	BLDG_EQUIP_SCH	PERIMETER_TOP_ZN_4	131.25	7.1	1412.289	10.76	199.921	0	0.5	0	0.5	General	0	1412.289
16	CORE_BOTTOM_ELEVATORS_EQUIP	BLDG_ELEVATORS	CORE_BOTTOM	983.54	52.9	32109.89	32.647	606.588	0	0.5	0	0.5	Elevators	0	22155.824

ZoneInfiltration Airflow Stats Nominal

	Name	Schedule Name	Zone Name	Zone Floor Area {m2}	# Zone Occupants	Design Volume Flow Rate {m3/s}	Volume Flow Rate/Floor Area {m3/s-m2}	Volume Flow Rate/Exterior Surface Area {m3/s-m2}	ACH - Air Changes per Hour	Equation A - Constant Term Coefficient {}	Equation B - Temperature Term Coefficient {1/C}	Equation C - Velocity Term Coefficient {s/m}	Equation D - Velocity Squared Term Coefficient {s2/m2}
1	FIRSTFLOOR_PLENUM_INFILTRATION	INFIL_QUARTER_ON_SCH	FIRSTFLOOR_PLENUM	1660.73	0	0.06126	3.689E-05	0.000302	0.109	1	0	0	0
2	MIDFLOOR_PLENUM_INFILTRATION	INFIL_QUARTER_ON_SCH	MIDFLOOR_PLENUM	1660.73	0	0.06126	3.689E-05	0.000302	0.109	1	0	0	0
3	PERIMETER_BOT_ZN_1_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_BOT_ZN_1	207.34	11.2	0.04135	0.0001994	0.000302	0.262	1	0	0	0
4	PERIMETER_BOT_ZN_2_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_BOT_ZN_2	131.26	7.1	0.02757	0.00021	0.000302	0.276	1	0	0	0
5	PERIMETER_BOT_ZN_3_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_BOT_ZN_3	207.34	11.2	0.04135	0.0001994	0.000302	0.262	1	0	0	0
6	PERIMETER_BOT_ZN_4_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_BOT_ZN_4	131.25	7.1	0.02757	0.00021	0.000302	0.276	1	0	0	0
7	PERIMETER_MID_ZN_1_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_MID_ZN_1	207.34	11.2	0.04135	0.0001994	0.000302	0.262	1	0	0	0
8	PERIMETER_MID_ZN_2_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_MID_ZN_2	131.26	7.1	0.02757	0.00021	0.000302	0.276	1	0	0	0
9	PERIMETER_MID_ZN_3_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_MID_ZN_3	207.34	11.2	0.04135	0.0001994	0.000302	0.262	1	0	0	0
10	PERIMETER_MID_ZN_4_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_MID_ZN_4	131.25	7.1	0.02757	0.00021	0.000302	0.276	1	0	0	0
11	PERIMETER_TOP_ZN_1_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_TOP_ZN_1	207.34	11.2	0.04135	0.0001994	0.000302	0.262	1	0	0	0
12	PERIMETER_TOP_ZN_2_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_TOP_ZN_2	131.26	7.1	0.02757	0.00021	0.000302	0.276	1	0	0	0
13	PERIMETER_TOP_ZN_3_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_TOP_ZN_3	207.34	11.2	0.04135	0.0001994	0.000302	0.262	1	0	0	0
14	PERIMETER_TOP_ZN_4_INFILTRATION	INFIL_QUARTER_ON_SCH	PERIMETER_TOP_ZN_4	131.25	7.1	0.02757	0.00021	0.000302	0.276	1	0	0	0
15	TOPFLOOR_PLENUM_INFILTRATION	INFIL_QUARTER_ON_SCH	TOPFLOOR_PLENUM	1660.73	0	0.563	0.0003389	0.000302	1.001	1	0	0	0

Zone Ventilation Parameters

	AirLoop Name	People Outdoor Air Rate - Rp [m3/s-person]	Zone Population - Pz	Area Outdoor Air Rate - Ra [m3/s-m2]	Zone Floor Area - Az [m2]	Breathing Zone Outdoor Airflow - Vbz [m3/s]	Cooling Zone Air Distribution Effectiveness - Ez-clg	Cooling Zone Outdoor Airflow - Voz-clg [m3/s]	Heating Zone Air Distribution Effectiveness - Ez-htg	Heating Zone Outdoor Airflow - Voz-htg [m3/s]
CORE_BOTTOM	VAV_1	0.0125	52.9352	0	983.54	0.6617	1	0.6617	1	0.6617
CORE_MID	VAV_2	0.0125	52.9352	0	983.54	0.6617	1	0.6617	1	0.6617
CORE_TOP	VAV_3	0.0125	52.9352	0	983.54	0.6617	1	0.6617	1	0.6617
PERIMETER_BOT_ZN_1	VAV_1	0.0125	11.1592	0	207.34	0.1395	1	0.1395	1	0.1395
PERIMETER_BOT_ZN_2	VAV_1	0.0125	7.0647	0	131.26	0.0883	1	0.0883	1	0.0883
PERIMETER_BOT_ZN_3	VAV_1	0.0125	11.1592	0	207.34	0.1395	1	0.1395	1	0.1395
PERIMETER_BOT_ZN_4	VAV_1	0.0125	7.0642	0	131.25	0.0883	1	0.0883	1	0.0883
PERIMETER_MID_ZN_1	VAV_2	0.0125	11.1592	0	207.34	0.1395	1	0.1395	1	0.1395
PERIMETER_MID_ZN_2	VAV_2	0.0125	7.0647	0	131.26	0.0883	1	0.0883	1	0.0883
PERIMETER_MID_ZN_3	VAV_2	0.0125	11.1592	0	207.34	0.1395	1	0.1395	1	0.1395
PERIMETER_MID_ZN_4	VAV_2	0.0125	7.0642	0	131.25	0.0883	1	0.0883	1	0.0883
PERIMETER_TOP_ZN_1	VAV_3	0.0125	11.1592	0	207.34	0.1395	1	0.1395	1	0.1395
PERIMETER_TOP_ZN_2	VAV_3	0.0125	7.0647	0	131.26	0.0883	1	0.0883	1	0.0883
PERIMETER_TOP_ZN_3	VAV_3	0.0125	11.1592	0	207.34	0.1395	1	0.1395	1	0.1395
PERIMETER_TOP_ZN_4	VAV_3	0.0125	7.0642	0	131.25	0.0883	1	0.0883	1	0.0883

Zone Ventilation Calculations for Cooling Design

	AirLoop Name	Box Type	Zone Primary Airflow - Vpz [m3/s]	Zone Discharge Airflow - Vdz [m3/s]	Minimum Zone Primary Airflow - Vpz-min [m3/s]	Zone Outdoor Airflow Cooling - Voz-clg [m3/s]	Primary Outdoor Air Fraction - Zpz	Primary Air Fraction - Ep	Secondary Recirculation Fraction- Er	Supply Air Fraction- Fa	Mixed Air Fraction - Fb	Outdoor Air Fraction - Fc	Zone Ventilation Efficiency - Evz
CORE_BOTTOM	VAV_1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	3.5786	3.5786	1.0736	0.6617	0	1	0	0	0	0	1
CORE_MID	VAV_2	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	3.4699	3.4699	1.041	0.6617	0	1	0	0	0	0	1
CORE_TOP	VAV_3	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	3.2904	3.2904	0.9871	0.6617	0	1	0	0	0	0	1
PERIMETER_BOT_ZN_1	VAV_1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.941	0.941	0.2823	0.1395	0	1	0	0	0	0	1
PERIMETER_BOT_ZN_2	VAV_1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.9584	0.9584	0.2875	0.0883	0	1	0	0	0	0	1
PERIMETER_BOT_ZN_3	VAV_1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.5948	0.5948	0.1784	0.1395	0	1	0	0	0	0	1
PERIMETER_BOT_ZN_4	VAV_1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	1.1148	1.1148	0.3344	0.0883	0	1	0	0	0	0	1
PERIMETER_MID_ZN_1	VAV_2	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	1.1845	1.1845	0.3554	0.1395	0	1	0	0	0	0	1
PERIMETER_MID_ZN_2	VAV_2	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	1.1384	1.1384	0.3415	0.0883	0	1	0	0	0	0	1
PERIMETER_MID_ZN_3	VAV_2	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.8186	0.8186	0.2456	0.1395	0	1	0	0	0	0	1
PERIMETER_MID_ZN_4	VAV_2	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	1.276	1.276	0.3828	0.0883	0	1	0	0	0	0	1
PERIMETER_TOP_ZN_1	VAV_3	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	1.1755	1.1755	0.3526	0.1395	0	1	0	0	0	0	1
PERIMETER_TOP_ZN_2	VAV_3	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	1.0727	1.0727	0.3218	0.0883	0	1	0	0	0	0	1
PERIMETER_TOP_ZN_3	VAV_3	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.9108	0.9108	0.2732	0.1395	0	1	0	0	0	0	1
PERIMETER_TOP_ZN_4	VAV_3	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	1.3253	1.3253	0.3976	0.0883	0	1	0	0	0	0	1

Zone Ventilation Calculations for Heating Design

	AirLoop Name	Box Type	Zone Primary Airflow - Vpz [m3/s]	Zone Discharge Airflow - Vdz [m3/s]	Minimum Zone Primary Airflow - Vpz-min [m3/s]	Zone Outdoor Airflow Heating - Voz-htg [m3/s]	Primary Outdoor Air Fraction - Zpz	Primary Air Fraction - Ep	Secondary Recirculation Fraction- Er	Supply Air Fraction- Fa	Mixed Air Fraction - Fb	Outdoor Air Fraction - Fc	Zone Ventilation Efficiency - Evz
CORE_BOTTOM	VAV_1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	1.0736	1.0736	1.0736	0.6617	1	1	0	0	0	0	1
CORE_MID	VAV_2	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	1.041	1.041	1.041	0.6617	1	1	0	0	0	0	1
CORE_TOP	VAV_3	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.9871	0.9871	0.9871	0.6617	0.5819	1	0	0	0	0	1
PERIMETER_BOT_ZN_1	VAV_1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.2823	0.2823	0.2823	0.1395	0.3472	1	0	0	0	0	1
PERIMETER_BOT_ZN_2	VAV_1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.2875	0.2875	0.2875	0.0883	0.3319	1	0	0	0	0	1
PERIMETER_BOT_ZN_3	VAV_1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.1784	0.1784	0.1784	0.1395	0.3507	1	0	0	0	0	1
PERIMETER_BOT_ZN_4	VAV_1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.3344	0.3344	0.3344	0.0883	0.3299	1	0	0	0	0	1
PERIMETER_MID_ZN_1	VAV_2	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.3554	0.3554	0.3554	0.1395	0.3272	1	0	0	0	0	1
PERIMETER_MID_ZN_2	VAV_2	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.3415	0.3415	0.3415	0.0883	0.3128	1	0	0	0	0	1
PERIMETER_MID_ZN_3	VAV_2	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.2456	0.2456	0.2456	0.1395	0.3304	1	0	0	0	0	1
PERIMETER_MID_ZN_4	VAV_2	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.3828	0.3828	0.3828	0.0883	0.3119	1	0	0	0	0	1
PERIMETER_TOP_ZN_1	VAV_3	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.3526	0.3526	0.3526	0.1395	0.2309	1	0	0	0	0	1
PERIMETER_TOP_ZN_2	VAV_3	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.3218	0.3218	0.3218	0.0883	0.2236	1	0	0	0	0	1
PERIMETER_TOP_ZN_3	VAV_3	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.2732	0.2732	0.2732	0.1395	0.2322	1	0	0	0	0	1
PERIMETER_TOP_ZN_4	VAV_3	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.3976	0.3976	0.3976	0.0883	0.2234	1	0	0	0	0	1